AGY:	Department of Health and Environmental Control

FII:	4

FIV:	29

PRD:	20040123

EFD:	20050422

EXD:	20050328

REG:	2897

PRI:	1

PRV:	28

COM:	Medical Affairs Committee 	13 SMA

Agriculture, Natural Resources and Environmental Affairs Committee 20 HANR

RES:	688

STA:	Final

AUT:	44-55-10

SUB:	State Primary Drinking Water

HST:	2897

BY	DATE	ACTION DESCRIPTION	COM	VOL/ISSUE	EXP DATE	R. NUM

___	________	__________________________	_______	___________	__________	_______

-	20040123	Proposed Reg Published in SR		28/1

-	20040421	Received by Lt. Gov & Speaker			20040819 (subject to

sine die revision)

H	20040422	Referred to Committee 	HANR 20

S	20040421	Referred to Committee 	SMA 13

-	20040603	Revised Review Period Exp Dat			20050328

S	20050331	Resolution Intro to Approve	SMA 13			S688

-	20050328	Approved by:  Expiration Date		29/4

TXT:

Document No. 2897

DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL

CHAPTER 61

Statutory Authority: 1976 Code Section 44-55-10 et seq.

R. 61-58. State Primary Drinking Water Regulations

Synopsis:

This amendment of R.61-58 will specify cross connection control requirements for residential lawn irrigation systems and to clarify other existing cross connection control requirements.  The amendments are in accordance with recommendations made by the Lawn Irrigation Backflow Taskforce, which was formed at the request of the state legislature.  See discussion below for Section-by-Section Discussion and Statements of Need and Reasonableness and Rationale herein.

Section-by-Section Discussion of Revisions

SECTION				CHANGE

R.61-58.7.F (1)		Title added, renumbered and organized for clarity

R.61-58.7.F (2)		Title added and revised for clarity and to specify the minimum device required on low hazard cross connections

R.61-58.7.F (3)		Added to specify cross connection control requirements for residential lawn irrigation systems

R.61-58.7.F (4)		Title added and organized for clarity

R.61-58.7.F (5)		Title added

R.61-58.7.F (6)		Title added

R.61-58.7.F (7)		Title added and revised to exempt backflow prevention assemblies on residential lawn irrigation systems from annual testing requirement

R.61-58.7.F (8)		Title added

R.61-58.7.F (9)		Title added and wording revised for clarity

Instructions:  Replace R.61-58.7.F as shown below in the Text of Amendment.

Text of Amendment:

R.61-58.7.F:

F.	Cross Connection Control

(1)  General

(a) All public water systems shall initiate and maintain a viable cross connection control program.  Such a program shall consist of:

(i) Locating and eliminating unprotected cross connections.

(ii) Maintaining records pertaining to the location of existing backflow prevention assemblies, type

and size of each assembly and test results.

(b) No person shall install, permit to be installed or maintain any cross connection between a public water system and any other non-public water system, sewer or a line from any container of liquids or other substances, unless an approved backflow prevention device or assembly is installed between the public water system and the source of contamination.

(2) Low Hazard Cross Connections

A connection between an approved public water system and another water source not hazardous to health but not meeting the standards of the approved public water system and not cross-connected within its system with a potentially dangerous substance shall be considered a low hazard category cross connection. At a minimum, an approved Double Check Valve Assembly or Pressure Vacuum Breaker must be installed on a low hazard cross connection except as provided for in section 3 below.

(3) Residential Lawn Irrigation Systems

(a) Low hazard residential lawn irrigation systems - Each public water system which has low hazard residential irrigation systems directly or indirectly connected to their public water system must have a written low hazard residential lawn irrigation system cross connection control policy.  This policy must be documented in writing and must be approved by the governing body of the public water system. The policy must specify the minimum acceptable device for low hazard residential lawn sprinkler systems.  The minimum acceptable device for low hazard residential lawn sprinkler systems is a residential dual check.  If a water system specifies another backflow prevention assembly as the minimum acceptable protection for these cross connections, the policy must be approved by the governing body of the public water system with due opportunity being provided for public comment and participation.  The written policy must:

(i) identify the type of backflow prevention device or assembly that is required to be installed on low

hazard residential lawn irrigation system connections.

(ii) establish a schedule for the required testing of double check valve assemblies, or other testable

assembly, if testable assemblies are  designated by the policy as minimum acceptable protection for low hazard residential lawn irrigation systems.  The minimum testing frequency must be specified in the policy and appropriate records must be maintained to verify compliance with the established testing requirements.

(iii) establish a schedule for the required change out of residential dual checks if these are the devices

designated by the policy as minimum acceptable protection for low hazard residential lawn irrigation systems. The minimum change out frequency must be specified in the policy and appropriate records must be maintained to verify compliance with the established change out requirements.

(b) High hazard residential lawn irrigation systems – Any residential lawn irrigation system that includes chemical addition, or is also connected to another water source which is not an approved public water system, shall be considered a high hazard cross connection and must meet the requirements of paragraph (4) below.

(4) High Hazard Cross Connections

(a) A connection between an approved public water system and a service or other water system which has or may have any material in the water dangerous to health, or connected to any material dangerous to health, that is or may be handled under pressure, or subject to negative pressure, shall be considered a high hazard category cross connection.  Protection shall be by air gap separation or an approved reduced pressure principle backflow prevention assembly.

(b)  Reduced pressure principal backflow prevention assemblies shall not be installed in any location subject to possible flooding.  This includes pits or vaults which are not provided with a gravity drain to the ground's surface that is capable of exceeding the discharge rate of the relief valve.

(5)  Fire Sprinkler Systems

Fire line sprinkler systems, except those in the high hazard category shall be protected by an approved double check valve assembly.  High hazard category fire sprinkler systems shall include, but not be limited to: antifreeze systems, foam systems, systems charged from or tied into ponds, lakes, streams, or any water source other than the approved public water supply.  High hazard category fire sprinkler systems shall comply with the requirements of Paragraph (4) above.

(6) Approved Devices and Assemblies

The Department shall prepare and publish a list of backflow prevention assemblies approved by the Department for use in South Carolina, and this list shall be updated at least once annually.

(7) Testing Requirements

When double check valve assemblies, pressure vacuum breakers, and/or reduced pressure principal backflow prevention assemblies are installed to protect a public water system against the possibility of backflow from a customer's water service, routine testing of the assemblies shall be performed by a certified tester.

(a) Each assembly shall be tested by a certified tester after installation and before use by the customer.  Except as specified in paragraph 3(a)(ii) above, each assembly shall be tested at least once annually by a certified tester.

(b) The public water system is to receive a written report of the inspection and testing results for all assemblies tested within its distribution system.  The report shall be submitted by the certified tester making the inspection and test.

(c) All backflow prevention assemblies shall be tested immediately after repairs of any kind are made to the assembly.

(8) Backflow Prevention Tester Certification

There are four (4) types of certified testers of backflow prevention assemblies; General Tester, Limited Tester, Inspector Tester and Manufacturer's Agent.  The definition of each type of certified tester is specified in R.61-58(A).

(a)	Each certified tester's license shall expire three (3) years from the date of issue.  In order to renew this certification for three (3) more years, the tester shall come before a designated person approved by the Department and shall successfully complete a written examination with a passing score of 70%, and perform the prescribed test on an approved reduced pressure principal backflow prevention assembly, double check valve assembly, and a pressure vacuum breaker using the tester's own differential pressure gauge.  The gauge must be accurate within 2% of full scale or plus or minus 0.3 pounds per square inch differential (PSID).  Any gauge found to be inaccurate or malfunctioning will be required to be calibrated or repaired as needed to bring it into compliance before certification will be renewed.

(b) Any applicant for certification who fails to properly perform the above prescribed tests will have his certification revoked immediately and will have to successfully complete the state sponsored backflow prevention training and certification course in order to become re-certified as a tester of backflow prevention assemblies in South Carolina.

(c) A certified tester may have his tester's certification revoked due to incompetence or falsification of test results, as determined by the Department.

(d) The Department shall reserve the right to charge or allow for the charge of a nominal fee for the administration of the recertification of testers.  This fee shall not exceed fifty dollars ($50.00).

(9) Installation of Pressure Vacuum Breakers

Where used, pressure vacuum breakers shall be installed at a minimum of twelve (12) inches above the highest downstream piping and shall not be subject to backpressure.

Fiscal Impact Statement:

There will be minimal cost to the state and its political subdivisions. See Statement of Need and Reasonableness below.

Statement of Need and Reasonableness:

The Statement of Need and Reasonableness was determined by staff analysis pursuant to S.C. Code Section 1-23-115(C)(1)-(3) and (9)-(11):

DESCRIPTION OF REGULATION:	Amendment to Regulation 61-58, State Primary Drinking Water Regulations

Purpose:	This amendment revises R.61-58 in order to adopt new backflow prevention requirements for residential lawn irrigation systems.  This amendment was proposed to address recommendations of the Lawn Irrigation Backflow Taskforce which was formed at the request of the state legislature to address inconsistencies in the statewide implementation of cross connection control requirements for residential lawn irrigation systems by public water systems.

Legal Authority: The State Primary Drinking Water Regulations are authorized by S.C. Code Ann.  44-55-10 et.  seq., State Safe Drinking Water Act.

Plan for Implementation:  These amendment will be incorporated within R.61-58 upon approval of the General Assembly and publication in the State Register.  This amendment will be implemented in the same manner in which the existing regulation is implemented.

DETERMINATION OF NEED AND REASONABLENESS OF THE REGULATION BASED ON ALL FACTORS HEREIN AND EXPECTED BENEFITS:

The adoption of these regulations, which address backflow prevention requirements for residential lawn irrigation systems, will address some of the recommendations of the Lawn Irrigation Taskforce which was formed at the request of the state legislature.

DETERMINATION OF COSTS AND BENEFITS:  The changes to backflow prevention requirements for residential lawn irrigation systems should not result in any major expenses for public water systems in the state.  Private citizens may realize a financial benefit if systems decide to implement the less stringent requirements included in this proposed amendment.  There will be no costs to the state or its political subdivisions.

UNCERTAINTIES OF ESTIMATES:  minimal

EFFECT ON ENVIRONMENT AND HEALTH:  The amendments would offer an option for water systems to implement less protective backflow prevention protection for residential lawn sprinkler systems.  It is difficult to determine if there would actually be a detrimental effect on public health as a result of this amendment. There will be no detrimental effect on the environment as a result of this amendment.

DETRIMENTAL EFFECT ON THE ENVIRONMENT AND PUBLIC HEALTH IF THE REGULATION IS NOT IMPLEMENTED:  There will be no detrimental effect on the environment if the amendments are not implemented.

Statement of Rationale:

The Statement of Rationale was developed by staff pursuant to S.C. Code Section 1-23-120:

In 2002, the state legislature asked the Department to form a taskforce to study the issue of backflow prevention protection for residential lawn irrigation systems and report back to them with the finding of the taskforce.  The taskforce included representatives from water utilities, backflow experts, consumer advocates and concerned citizens.  The taskforce met a total of four times and, as a result, the Department produced a report entitled Lawn Irrigation Backflow Taskforce: Report to The Legislature.  This proposed amendment is intended to address the recommendations of the taskforce, which are outlined in the report.