Agency Name: Building Codes Council - Labor, Licensing and Regulation

Statutory Authority: 6-9-40 and 40-1-70

Document Number: 5426

Proposed in State Register Volume and Issue: 49/10

House Committee: Reg., Admin. Procedures, AI and Cybersecurity

Senate Committee: Labor, Commerce and Industry Committee

110 Day Review Expiration Date for Automatic Approval: 05/03/2026

Status: Pending

Subject: International Fire Code

History: 5426

By	Date	Action Description	Jt. Res. No.	Expiration Date

-	10/24/2025	Proposed Reg Published in SR

-	01/13/2026	Received President of the Senate & Speaker		05/03/2026

S	01/13/2026	Referred to Committee

H	01/14/2026	Referred to Committee

S	03/31/2026	Resolution Introduced to Approve	1074

Document No. 5426

DEPARTMENT OF LABOR, LICENSING AND REGULATION

BUILDING CODES COUNCIL

CHAPTER 8

Statutory Authority: 1976 Code Sections 6-9-40 and 40-1-70

8-900. International Fire Code.

Synopsis:

The South Carolina Building Codes Council proposes to amend Chapter 8, Article 9, to reflect modifications to the 2024 South Carolina Building Codes, the International Fire Code.

A Notice of Drafting was published in the State Register on June 27, 2025.

Instructions:

Print regulation as shown below. All other items remain unchanged.

Indicates Matter Stricken

Indicates New Matter

Text:

ARTICLE 9

International Fire Code

20214 International Fire Code Modification Summary

(Statutory Authority: 1976 Code Section 6-9-40)

8-900. International Fire Code.

NOTE-This article is based upon the International Fire Code, 20214 Edition, in accordance with the statutory amendments to acts governing the Building Codes Council, except for the modifications referenced below.

This code is identical to the 20214 Edition of the International Fire Code except for the following modifications:

8-901. IFC Section 202 General definitions.

Recreational Fire: An outdoor fire burning materials other than rubbish where the fuel being burned is not contained in an incinerator, outdoor fireplace, portable outdoor fireplace, barbeque grill or barbeque pit and has a total fuel area of 3 feet (914 mm) or less in diameter and 2 feet (610 mm) or less in height for pleasure, religious, ceremonial to include sky lanterns, cooking, warmth or similar purposes.

8-902. IFC Section 202 General definitions.

Primitive Camp Structure: Shall include any structure permanent or temporary in nature, used for outdoor camping (transient), open on at least one side with no fully enclosed habitable spaces, less than 400 square feet under roof, and not classified as a residential occupancy due to lack of electrical, plumbing, mechanical and sprinkler systems.

8-903. IFC Section 202203.2.8 General definitionsAssembly Group A-3.

Add to the listing of A-3 occupancies: Structures, without a commercial kitchen, used in agritourism activity as defined by S.C. Code Ann. 46-53-10(1).

8-904. IFC Section 315.3.3 Equipment rooms. Combustible Mmaterial shall not be stored in boiler rooms, mechanical rooms, elevator machine rooms, electrical equipment rooms or in fire command centers as specified in Section 508.1.5. Rooms shall be labeled with appropriate signage “No storage allowed.”

8-905. IFC Section 319.11 Clearance requirements.

Mobile cooking operations shall be separated from buildings, structures, canopies, tents, combustible materials, vehicles, and other cooking operations by a minimum of 10 feet. Exhaust shall be directed away from openings, air intakes, and away from any means of egress.

8-9065. IFC Section 503.1.2 Additional access.

The fire code official is authorized to require more than one fire apparatus access road based on the potential for impairment of a single road by vehicle congestion, condition of terrain, climatic conditions or other factors that could limit access.

Exception: Where two fire apparatus access roads are required by Section 503.1.2 or this appendix, the additional fire apparatus access road is permitted to be a driveway, pathway, court or other approved fire lane not accessible to public motor vehicles, where designed by a registered design professional to meet the loading requirements and minimum specifications of Section 503 and this appendix, and the surface provides all-weather driving capabilities. Marking or signs shall be provided in accordance with Section 503.3 and Section D103.6.

8-9086. IFC Section 503.2.1 Dimensions.

Fire apparatus access roads shall have an unobstructed width of not less than 20 feet (6096 mm) except for approved security gates in accordance with Section 503.6 and an unobstructed vertical clearance of not less than 13 feet 6 inches (4115 mm).

8-907. IFC Section 503.1.2.1 One- or two-family dwelling residential developments having less than 50 units.

Developments of one- or two-family dwellings where the number of dwelling units does not exceed 50 shall be permitted to have a single approved fire apparatus access road provided all of the following requirements are met:

1. The minimum unobstructed width of the single fire apparatus access road shall be 26 feet (7925 mm) and shall otherwise comply with Section 503.

2. A minimum of one fire hydrant on each side of the fire apparatus access road in accordance with Section 507.5 shall be provided. The fire code official shall be permitted to require additional hydrants and hydrant spacing based on the length of the fire apparatus access road, fire flow requirements, and the distance from any point on the street or road frontage to a hydrant.

3. The development is not located in a wildland-urban interface area as defined in the International Wildland-Urban Interface Code.

Future Development. The number of dwelling units on a single fire apparatus access road shall not be increased unless fire apparatus access roads will connect with future development, as determined by the fire code official.Repealed.

8-9098. IFC Section 507.1 Required water supply.

An approved water supply capable of supplying the required fire flow for fire protection shall be provided to premises on which facilities, buildings, or portions of buildings are hereafter constructed or moved into or within the jurisdiction to meet the necessary fire flow as determined by the fire code official. Where public water supply is inadequate or not available, an approved alternate water source meeting the fire flow requirements shall be provided. Fire flow performance tests shall be witnessed by the fire code official or representative prior to final approval.

Exception. One- and two-family dwellings, including attached or detached accessory structures.

8-9109. IFC Section 507.5.1 Where required.

Where a portion of the facility or building hereafter constructed or moved into or within the jurisdiction is more than 500 feet (152 m) from a hydrant on a fire apparatus access road, as measured by an approved route around the exterior of the facility or building, on-site fire hydrants and mains shall be provided where required by the fire code official.

Location. The location and number of hydrants shall be designated by the fire official, but in no case shall the distance between installed fire hydrants exceed 1000 feet (305 m). Fire hydrants shall be located within 500 feet (152 m) of all fire fighter access points when measured along the normal routes of fire department vehicle access which conforms to the requirements of Section 503. No point of the exterior of a building shall be located more than 500 feet (152 m) from a hydrant accessible to fire department vehicles as provided in Section 503.

Exceptions:

1. For Group R-3 and Group U occupancies, the distance requirement shall be 600 feet (183 m).

2. For buildings equipped throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the distance requirement shall be 600 feet (183 m).

8-9110. IFC Section 507.5.1.1 Hydrant for standpipe systems.

Buildings equipped with a standpipe or fire sprinkler system installed in accordance with Section 903 or 905 shall have a fire hydrant within 100 feet (30 480 mm) of the fire department connections.

Exception: The distance shall be permitted to exceed 100 feet (30 480 mm) where approved by the fire code official.

8-9121. IFC Section 507.5.4 Obstruction.

Unobstructed access to fire hydrants shall be maintained at all times. The fire department shall not be deterred or hindered from gaining immediate access to fire protection equipment or fire hydrants. No parking shall be allowed within 15 feet (4572 mm) of a fire hydrant.

8-912. IFC Section 606.3.3.2. Grease accumulation.

If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned in accordance with ANSI/IKECA C10 and NFPA 96. The cleanings shall be completed by a properly trained and qualified company or person(s) acceptable to the authority having jurisdiction. The individual or company performing the inspections and cleaning shall indicate their certifications to the authority having jurisdiction upon request.

8-913. IFC Section 607.1 General.

Storage of cooking oil (grease) in commercial cooking operations utilizing above-ground tanks with a capacity greater than 60 gal (227 L) installed within a building shall comply with Sections 607.2 through 607.7 and NFPA 30. For purposes of this section, cooking oil shall be classified as a Class IIIB liquid unless otherwise determined by testing. These tanks shall have the contents identified as outlined in Section 5703.5.

8-914. IFC Section 901.6.3 Records.

Records of all system inspections, tests, and maintenance required by the referenced standards shall be maintained in accordance with Section 110.3. Copies of the inspection reports shall be sent to the local jurisdiction by the servicing vendor as prescribed by the Ffire Ccode Oofficial.

8-915. IFC Section 904.14. Commercial cooking systems.

The automatic fire-extinguishing system for commercial cooking systems shall be of a type recognized for protection of commercial cooking equipment and exhaust systems of the type and arrangement protected. Preengineered automatic dry- and wet-chemical extinguishing systems shall be tested in accordance with UL300 and listed and labeled for the intended application. Other types of automatic fire-extinguishing systems shall be listed and labeled for specific use as protection for commercial cooking operations. The system shall be installed and maintained in accordance with this code, NFPA 96, its listing and the manufacturer’s installation instructions. Automatic fire-extinguishing systems of the following types shall be installed and maintained in accordance with the referenced standard indicated, as follows:

1.	Carbon dioxide extinguishing systems, NFPA 12.

2.	Automatic sprinkler systems, NFPA 13.

3.	Automatic water mist systems, NFPA 750.

4.	Foam-water sprinkler system or foam-water spray systems, NFPA 11.

5.	Dry-chemical extinguishing systems, NFPA 17.

6.	Wet-chemical extinguishing systems, NFPA 17A.

Exception: Factory-built commercial cooking recirculating systems that are tested in accordance with UL 710B and listed, labeled and installed in accordance with Section 304.1 of the International Mechanical Code.

8-9156. IFC Section 907.6.5 Access.

Access shall be provided to each fire alarm device and notification appliance for periodic inspection, maintenance and testing. Fire alarm notification devices shall be unobstructed and visible at all times.

8-9167. IFC Section 1010.2.143 Controlled egress doors in Groups I-1, and I-2, as well asand I-4 (Adult Day Care occupancy only).

Controlled egress Eelectrical locking systems, including electro-mechanical locking systems and electromagnetic locking systems where egress is controlled by authorized personnel, shall be permitted on doors to be locked in the means of egress in Group I-1, and I-2, and I-4 (Adult Day Care occupancy only) occupancies where the clinical needs of persons receiving care require their containment. and Group I-4 Adult Day Care occupancies where the clinical needs of person receiving care require their containment. Controlled egress doors shall be permitted in such occupancies where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke detection system installed in accordance with Section 907, provided that the doors are installed and operate in accordance with all of the following:

1. The door’s electric locks shall unlock on actuation of the automatic sprinkler system or automatic smoke detection system allowing immediate free egress.

2. The door’s electric locks shall unlock on loss of power to the electrical locking system or to the electric lock mechanism allowing immediate free egress. controlling the lock or lock mechanism.

3. The doorelectric locking system shall be installed to have the capability of being unlockedunlocking the electric locks by a switch located at the fire command center, a nursing station or other approved location. The switch shall directly break power to the electric lock.

4. A building occupant shall not be required to pass through more than one door equipped with a controlled egress locking system before entering an exit.

5. The procedures for unlocking the doors shall be described and approved as part of the emergency planning and preparedness required by Chapter 4 of the International Fire Code.

6. All clinical staff shall have the keys, codes or other means necessary to operate the controlled egress electrical locking systems.

7. Emergency lighting shall be provided at the door.

8. The electromechanical or electromagnetic door locking systemdevice units shall be listed in accordance with either UL 294 or UL 1034.

Exceptions:

1. Items 1 through 4 shall not apply to doors to areas occupied by persons who, because of clinical needs, require restraint or containment as part of the function of a psychiatric or cognitive treatment area.

2. Items 1 through 4 shall not apply to doors to areas where a listed egress control system is utilized to reduce the risk of child abduction from nursery and obstetric areas of a Group I-2 hospital.

8-9178. IFC 1016.2 Egress through intervening spaces.

Egress through intervening spaces shall comply with this section.

1. Exit access through an enclosed elevator lobby is permitted. Where access to two or more exits or exit access doorways is required in Section 1006.2.1, access to not less than one of the required exits shall be provided without travel through the enclosed elevator lobbies required by Section 3006 of the South Carolina Building Code. Where the path of exit access travel passes through an enclosed elevator lobby, the level of protection required for the enclosed elevator lobby is not required to be extended to the exit unless direct access to an exit is required by other sections of this code.

2. In other than Group H occupancies, Eegress from a room or space shall notis allowed to pass through adjoining or intervening rooms or areas provided that, except where such adjoining rooms or areas and the area served are accessory to one or the other and, are not a Group H occupancy and provide a discernible path of egress travel to an exit.

Exception: Means of egress are not prohibited through adjoining or intervening rooms or spaces in a Group H, S, or F occupancy where the adjoining or intervening rooms or spaces are the same or a lesser hazard occupancy group.

3.	In Group H occupancies, egress from a room or space is allowed to pass through adjoining or intervening rooms or areas provided that such adjoining rooms or areas are the same or lesser hazard occupancy group and provide a discernible path of egress travel to an exit.

34. An exit access shall not pass through a room that can be locked to prevent egress.

Exception: An electrically locked exit access door providing egress from an elevator lobby shall be permitted in accordance with Section 1010.2.14.

45. Means of egress from dwelling units or sleeping areas shall not lead through other sleeping areas, toilet rooms or bathrooms.

Exception: Dwelling units or sleeping areas in R-1 and R-2 occupancies shall be permitted to egress through other sleeping areas serving adjoining rooms that are part of the same dwelling unit or guest room.

56. Egress shall not pass through kitchens, storage rooms, closets, or spaces used for similar purposes.

Exceptions:

1. Means of egress are not prohibited through a kitchen area serving adjoining rooms constituting part of the same dwelling unit or sleeping unit.

2. Means of egress are not prohibited through stockrooms in Group M occupancies where all of the following are met:

2.1 The stock is of the same hazard classification as that found in the main retail area.

2.2 Not more than 50 percent of the exit access is through the stockroom.

2.3 The stockroom is not subject to locking from the egress side.

2.4 There is a demarcated, minimum 44-inch-wide (1118 mm) aisle defined by a wall not less than 42 inches (1067 mm) high or similar construction that will maintain the required width and lead directly from the retail area to the exit without obstructions.

8-919. IFC Section 1032.11. Maintenance of the listed occupancy load signage.

Design occupancy load maintenance: the designed occupancy load calculations shall be adhered to and posted per requirements outlined in Section 1004.1 through 1004.9. Any changes to the occupancy load shall be designed and submitted to the building department for review and approval.

8-920. IFC Section 2303.2 Emergency disconnect switches.

An approved emergency disconnect switch shall be provided at an approved location to stop the transfer of fuel to the fuel dispensers in the event of a fuel spill or other emergency. The emergency disconnect switch for exterior fuel dispensers shall be provided with ready access and shall be located within 100 feet (30 480 mm) of, but not less than 20 feet (6096 mm) from, the fuel dispensers. For interior fuel-dispensing operations, the emergency disconnect switch shall be provided with ready access and be installed at an approved location. Such devices shall be distinctly labeled as “EMERGENCY FUEL SHUTOFF”. Signs shall be provided in approved locations. The sign shall be durable with lettering not less than two inches in size. Letter widths, strokes and spacing shall be in proportion to their height. The sign shall be red in color with white lettering, or a white sign with red lettering. The sign shall state EMERGENCY FUEL SHUTOFF.

8-91821. IFC Section 2303.2.2 Testing.

Emergency disconnect switches shall be tested annually by the responsible party to ensure proper operation; records of testing shall be maintained on site for inspection. For Aany switches determined to be faulty, the fuel pumps they serve shall be taken out of service until the emergency shutoff switch is placed back into service.

8-922. IFC Section 2304.3.6. Communications.

A telephone not requiring a coin to operate or other approved, clearly identified means to notify the fire department shall be provided on the site in a location approved by the fire code official. This means of communication shall be maintained and tested annually. Test records shall be maintained and submitted to the fire code official.

8-91923. IFC Section 2305.5 Fire extinguishers.

Approved portable fire extinguishers complying with Section 906 with a minimum rating of 2-A:20-B:C shall be provided and located such that an extinguisher is not more than 50 feet (15 240 mm) from pumps, dispensers or storage tank fill-pipe openings.

8-92024. IFC Section 2307.4 Location of dispensing operations and equipment.

The point of transfer for LP-gas dispensing operations shall be separated from buildings and other exposures in accordance with NFPA 58 Table 6.7.2.1 and IFC Section 2306.7.

Exception: The point of transfer for LP-gas dispensing operations need not be separated from canopies that are constructed in accordance with the South Carolina Building Code and that provide weather protection for the dispensing equipment.

LP-gas containers shall be located in accordance with Chapter 61. LP-gas storage and dispensing equipment shall be located outdoors and in accordance with Section 2306.7.

8-92125. IFC Section 2307.7 Public fueling of motor vehicles.

Self-service LP-gas dispensing systems, including key, code and card lock dispensing systems, shall be limited to the filling of permanently mounted containers providing fuel to the LP-gas powered vehicle, is removed.

The requirements for self-service LP-gas dispensing systems shall be in accordance with the following:

1.	The arrangement and operation of the transfer of product into a vehicle shall be in accordance with this section and Chapter 61.

2.	The system shall be provided with an emergency shutoff switch located within 100 feet (30 480 mm) of, but not less than 20 feet (6096 mm) from, dispensers.

3.	The owner of the LP-gas motor fuel-dispensing facility or the owner’s designee shall provide for the safe operation of the system and the training of users.

4.	The dispenser and hose-end valve shall release not more than 1/8 fluid ounce (4 cc) of liquid to the atmosphere upon breaking the connection with the fill valve on the vehicle.

5.	Portable fire extinguishers shall be provided in accordance with Section 2305.6.

6.	Warning signs shall be provided in accordance with Section 2305.6.

7.	The area around the dispenser shall be maintained in accordance with Section 2305.7.

8-926. IFC Section 4106.6 Clearance requirements.

Mobile cooking operations shall be separated from buildings, structures, canopies, tents, combustible materials, vehicles, and other cooking operations by a minimum of 10 feet.

8-92227. IFC Section 6101.1 Scope.

Storage, handling and transportation of liquefied petroleum gas (LP-gas) and the installation of LP-gas equipment pertinent to systems for such uses shall comply with this chapter and NFPA 58. Properties of LP-gases shall be determined in accordance with Annex B of NFPA 58.

8-928. IFC Section 6104.2. Maximum capacity within established limits.

For the protection of heavily populated or congested areas, storage of liquefied petroleum gas shall not exceed an aggregate capacity in any one installation of 4,000 gallons (15 140 L) within the limits established by law as set forth in the fire code adoption ordinance or other regulation adopted by the jurisdiction.

Exception: In particular installations, this capacity limit shall be determined by the fire code official, after consideration of special features such as topographical conditions, nature of occupancy, and proximity to buildings, capacity of proposed LP-gas containers, degree of fire protection to be provided and capabilities of the local fire department.

8-92329. IFC Section 6106.1 Attendants.

Dispensing of LP-gas shall be performed by a qualified attendant that meets the requirements of this section and NFPA 58 Section 4.4.

8-930. IFC Section 6107.3 Clearance to combustibles.

Combustible materials shall not accumulate or be stored within 10 feet (3 m) of a container.

8-92431. IFC Section 6107.4 Protecting containers from vehicles.

Where exposed to vehicular damage due to proximity to alleys, driveways or parking areas, LP-gas containers, regulators and piping shall be protected in accordance with NFPA 58.

Exception: An alternative method may be used that meets the intent of this section with the approval of the authority having jurisdiction (AHJ).

8-92532. IFC Section 6109.13 Protection of containers.

LP-gas containers shall be stored within a suitable enclosure or otherwise protected against tampering. Vehicle impact protections shall be requiredprovided as required by the fire code official in accordance with Section 312 or Section NFPA 58 8.4.2.2.

Exception: Vehicle impact protection shall not be required for protection of LP-gas containers where the containers are kept in lockable, ventilated cabinets of metal construction.

8-92633. IFC Section 6110.1 Removed from service.

Containers not connected for service at customer locations. LP-gas containers at customers’ locations that are not connected for service shall comply with all of the following:

1. Have LP-gas container outlets, except relief valves, closed and plugged or capped.Containers shall be located in a manner that will minimize exposure to physical damage.

2. Be positioned with the relief valve in direct communication with the LP-gas container vapor space.Containers shall be oriented so that the pressure relief valve remains in communication with the vapor space.

3.	Containers shall not be located on roofs of buildings.

4.	Valve outlets on ASME containers shall be plugged or capped.

5.	Where screw-on-type caps or collars are utilized on ASME containers, they shall be in place wherever this type of container is stored regardless of the fill level of the container.

6.	The location of ASME containers shall comply with the “Aboveground Containers” column and the “Between Containers” column of NFPA 58 Table 6.4.1.1 with respect to important buildings and lines of adjoining property that can be built upon.

7.	Where the provisions of item 6 are impractical, alternative storage locations for containers shall be approved by the authority having jurisdiction.

8-92734. IFC Section 6111.2.1 Near residential, educational and institutional occupancies and other high-risk areas.

LP-gas tank vehicles shall not be left unattended at any time on residential streets or within 500 feet (152 m) of a residential area, apartment or hotel complex, educational facility, hospital or care facility. Tank vehicles shall not be left unattended at any other place that would, in the opinion of the fire code official, post an extreme life hazard.

Where vehicles carrying portable containers or cargo tank vehicles or 3500 gal (13 m3) water capacity or less are parked on streets adjacent to the driver’s residence in uncongested residential areas, the parking locations shall be at least 50 ft (15 m) from a building used for assembly, institutional, or multiple residential occupancy.

Separation distance requirements may be reduced to not less than 50 feet as approved by the fire code official, based upon a completed fire safety analysis and consideration of special features such as topographical conditions, capacity of the LP-gas vehicle and the capabilities of the local fire department. The Office of the State Fire Marshal will provide an approved fire safety analysis to be utilized for this specific requirement.

Fiscal Impact Statement:

There will be no cost incurred by the State or any of its political subdivisions for these regulations.

Statement of Rationale:

The South Carolina Building Codes Council proposes to amend Chapter 8, Article 9, to reflect modifications to the 2024 South Carolina Building Codes, the International Fire Code.