Agency Name: Building Codes Council - Labor, Licensing and Regulation

Statutory Authority: 6-9-40 and 40-1-70

Document Number: 5427

Proposed in State Register Volume and Issue: 49/10

House Committee: Reg., Admin. Procedures, AI and Cybersecurity

Senate Committee: Labor, Commerce and Industry Committee

110 Day Review Expiration Date for Automatic Approval: 05/03/2026

Status: Pending

Subject: International Fuel Gas Code

History: 5427

By	Date	Action Description	Jt. Res. No.	Expiration Date

-	10/24/2025	Proposed Reg Published in SR

-	01/13/2026	Received President of the Senate & Speaker		05/03/2026

S	01/13/2026	Referred to Committee

H	01/14/2026	Referred to Committee

S	03/31/2026	Resolution Introduced to Approve	1079

Document No. 5427

DEPARTMENT OF LABOR, LICENSING AND REGULATION

BUILDING CODES COUNCIL

CHAPTER 8

Statutory Authority: 1976 Code Sections 6-9-40 and 40-1-70

8-1000. International Fuel Gas Code.

Synopsis:

The South Carolina Building Codes Council proposes to amend Chapter 8, Article 10, to reflect modifications to the 2024 South Carolina Building Codes, the International Fuel Gas Code.

A Notice of Drafting was published in the State Register on June 27, 2025.

Instructions:

Print regulation as shown below. All other items remain unchanged.

Indicates Matter Stricken

Indicates New Matter

Text:

ARTICLE 10

International Fuel Gas Code

20214 International Fuel Gas Code Modification Summary

(Statutory Authority: 1976 Code Section 6-9-40)

8-1000. International Fuel Gas Code.

NOTE-This article is based upon the International Fuel Gas Code, 20214 Edition, in accordance with the statutory amendments to acts governing the Building Codes Council, except for the modifications referenced below.

This code is identical to the 20214 Edition of the International Fuel Gas Code except for the following modifications:

8-1001. IFGC Section 401.9 Identification.

This section is deleted without substitution.

8-1002. IFGC Section 401.10 Third-party testing and certification.

All piping, tubing and fittings shall comply with the applicable referenced standards, specifications and performance criteria of this code, including Section 403 of the South Carolina Fuel Gas Code and corresponding sections.

8-1003. IFGC Section 404.17.1 Limitations.

Plastic pipe and plastic composite piping including pex-al-pex and pe-al-pe (where listed and approved) shall be installed outdoors underground only. Plastic pipe shall not be used within or under any building or slab or be operated at pressures greater than 100 psig (689 kPa) for natural gas or 30 psig (207 kPa) for LP-gas.

Exceptions:

1.	Plastic pipe shall be permitted to terminate above ground outside of buildings where installed in premanufactured anodeless risers or service head adapter risers that are installed in accordance with the manufacturer’s instructions.

2. Plastic pipe shall be permitted to terminate with a wall head adapter within buildings where the plastic pipe is inserted in a piping material for fuel gas use in buildings.

3.	Plastic pipe shall be permitted under outdoor patio, walkway and driveway slabs provided that the burial depth complies with Section 404.12.

8-10034. IFGC Section 412.4 Listed equipment.

Hoses, hose connections, vehicle fuel connections, dispensers, LP-gas pumps and electrical equipment used for LP-gas shall comply with the requirements of NFPA 58.

8-10045. IFGC Section 412.6 Location.

In addition to the fuel dispensing requirements of the South Carolina Fire Code, the point of transfer for dispensing operations shall be 25 feet (7620 mm) or more from buildings having combustible exterior wall surfaces, buildings having noncombustible exterior wall surfaces that are not part of a 1-hour fire-resistance-rated assembly or buildings having combustible overhangs, property whichthat could be built on, and railroads; and at least 10 feet (3048 mm) from public streets or sidewalks and buildings having noncombustible exterior wall surfaces that are part of a fire-resistance-rated assembly having a rating of 1 hour or more; and 5 feet (1524 mm) from driveways.

Exceptions:

1. The point of transfer for LP-gas dispensing operations need not be separated from canopies providing weather protection for the dispensing equipment constructed in accordance with the International Building Code. Liquefied petroleum gas containers shall be located in accordance with the International Fire Code.

2. The separation from driveways is not required where the driveway serves the vehicle fuel dispenser.

Liquefied petroleum gas storage and dispensing equipment shall be located outdoors and in accordance with the South Carolina Fire Code.

8-10056. IFGC Section 412.8.3 Vehicle impact protection.

Where installed within 10 feet (3048 mm) of vehicle traffic, LP-gas storage containers, pumps and dispensers shall be protected in accordance with Section 2307.5, Item 2 of the South Carolina Fire Code.

Exception: An alternative method may be used that meets the intent of this section with the approval of the authority having jurisdiction (AHJ).

8-10067. IFGC Section 412.10 Private fueling of motor vehicles.

Self-service LP-gas dispensing systems, including key, code and card lock dispensing systems, shall not be open to the public. In addition to the requirements of the South Carolina Fire Code, self-service LP-gas dispensing systems shall be provided with an emergency shutoff switch located within 100 feet (30 480 mm) of, but not less than 20 feet (6096 mm) from, dispensers, and the owner of the dispensing facility shall ensure the safe operation of the system and the training of users.

8-10078. IFGC Section 505.1.1 Commercial cooking appliances vented by exhaust hoods.

Where commercial cooking appliances are vented by means of the Type I or Type II kitchen exhaust hood system that serves such appliances, the exhaust system shall be fan powered and the appliances shall be interlocked with the exhaust hood system to prevent appliance operation when the exhaust hood system is not operating. Where a solenoid valve is installed in the gas piping as part of an interlock system, gas piping shall not be installed to bypass such valve. Dampers shall not be installed in the exhaust system.

Exception: An interlock between the cooking appliance(s) and the exhaust hood system shall not be required for appliances that are of the manually operated type and are factory equipped with standing pilot burner ignition systems.

Fiscal Impact Statement:

There will be no cost incurred by the State or any of its political subdivisions for these regulations.

Statement of Rationale:

The South Carolina Building Codes Council proposes to amend Chapter 8, Article 10, to reflect modifications to the 2024 South Carolina Building Codes, the International Fuel Gas Code.